## LP-G
Size of Cable (mm2) | Panel Name:- LP-G C.B :- 10A Cable :- 4*3+3 mm2 | [18 empty] | Size of Cable (mm2)
Feeder From :- MDP Panel Location:- GROUND FLOOR
| Description | Load | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | AMP Trip | PH | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Load | Description
3*2.5 | Lighting | 124 | 124 |  |  | 1 | 10 | 1 |  |  |  | 2 | 10 | 1 | 102 |  |  | 102 | Lighting | 3*2.5
3*2.5 | Lighting | 60 |  | 60 |  | 1 | 10 | 3 |  |  |  | 4 | 10 | 1 |  | 198 |  | 198 | Lighting | 3*2.5
3*2.5 | Lighting | 198 |  |  | 198 | 1 | 10 | 5 |  |  |  | 6 | 10 | 1 |  |  | 171 | 171 | Lighting | 3*2.5
3*2.5 | Lighting | 118 | 118 |  |  | 1 | 10 | 7 |  |  |  | 8 | 10 | 1 | 96 |  |  | 96 | Lighting | 3*2.5
3*2.5 | Lighting | 118 |  | 118 |  | 1 | 10 | 9 |  |  |  | 10 | 10 | 1 |  | 177 |  | 177 | Lighting | 3*2.5
3*2.5 | Lighting | 198 |  |  | 198 | 1 | 10 | 11 |  |  |  | 12 | 10 | 1 |  |  | 147.5 | 147.5 | Lighting | 3*2.5
3*2.5 | Lighting | 192 | 192 |  |  | 1 | 10 | 13 |  |  |  | 14 | 10 | 1 | 118 |  |  | 118 | Lighting | 3*2.5
3*2.5 | Lighting | 177 |  | 177 |  | 1 | 10 | 15 |  |  |  | 16 |  | 1 |  | 0 |  |  | spare
| spare |  |  |  | 0 | 1 |  | 17 |  |  |  | 18 |  | 1 |  |  | 0 |  | spare
|  |  | 0 |  |  | 1 |  | 19 |  |  |  | 20 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 21 |  |  |  | 22 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 23 |  |  |  | 24 |  | 1 |  |  | 0
|  |  | 0 |  |  | 1 |  | 25 |  |  |  | 26 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 27 |  |  |  | 28 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 29 |  |  |  | 30 |  | 1 |  |  | 0
|  |  | 0 |  |  | 1 |  | 31 |  |  |  | 32 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 33 |  |  |  | 34 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 35 |  |  |  | 36 |  | 1 |  |  | 0
|  |  | 0 |  |  | 1 |  | 37 |  |  |  | 38 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 39 |  |  |  | 40 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 41 |  |  |  | 42 |  | 1 |  |  | 0
|  |  | 0 |  |  | 1 |  | 43 |  |  |  | 44 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 45 |  |  |  | 46 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 47 |  |  |  | 48 |  | 1 |  |  | 0
Sub-total |  |  | 434 | 355 | 396 |  |  |  | R | Y | B |  |  |  | 316 | 375 | 318.5 |  | Sub-total
connected load (KVA) |  |  | 0.434 | 0.355 | 0.396 | [9 empty] | 0.316 | 0.375 | 0.3185 |  | connected load (KW)
|  |  | 2.1945 | Kwatt | [8 empty] | Total connected load "R" |  |  |  | 750 |  | Watt
[13 empty] | Total connected load "Y" |  |  |  | 730 |  | Watt
|  |  | 0.9 | [9 empty] | Total connected load "B" |  |  |  | 714.5 |  | Watt
[13 empty] | Difference between max & min Ph |  |  |  | 35.5
[13 empty] | % Diffrence |  |  |  | 4.7333
|  |  | 1.9751 | Kwatt | [8 empty] | Panel Balance Check |  |  | BALANCED
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C

## LP-F
Size of Cable (mm2) | Panel Name:- LP-F C.B :- 10A Cable :- 4*3+3 mm2 | [18 empty] | Size of Cable (mm2)
Feeder From :- MDP Panel Location:- FIRST FLOOR
| Description | Load | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | AMP Trip | PH | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Load | Description
3*2.5 | Lighting | 200.5 | 200.5 |  |  | 1 | 10 | 1 |  |  |  | 2 | 10 | 1 | 96 |  |  | 96 | Lighting | 3*2.5
3*2.5 | Lighting | 147.5 |  | 147.5 |  | 1 | 10 | 3 |  |  |  | 4 | 10 | 1 |  | 198 |  | 198 | Lighting | 3*2.5
3*2.5 | Lighting | 150 |  |  | 150 | 1 | 10 | 5 |  |  |  | 6 | 10 | 1 |  |  | 155 | 155 | Lighting | 3*2.5
3*2.5 | Lighting | 200.5 | 200.5 |  |  | 1 | 10 | 7 |  |  |  | 8 | 10 | 1 | 177 |  |  | 177 | Lighting | 3*2.5
3*2.5 | Lighting | 118 |  | 118 |  | 1 | 10 | 9 |  |  |  | 10 | 10 | 1 |  | 177 |  | 177 | Lighting | 3*2.5
3*2.5 | Lighting | 206.5 |  |  | 206.5 | 1 | 10 | 11 |  |  |  | 12 | 10 | 1 |  |  | 177 | 177 | Lighting | 3*2.5
| spare |  | 0 |  |  | 1 |  | 13 |  |  |  | 14 |  | 1 | 0 |  |  |  | spare
| spare |  |  | 0 |  | 1 |  | 15 |  |  |  | 16 |  | 1 |  | 0 |  |  | spare
| spare |  |  |  | 0 | 1 |  | 17 |  |  |  | 18 |  | 1 |  |  | 0 |  | spare
|  |  | 0 |  |  | 1 |  | 19 |  |  |  | 20 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 21 |  |  |  | 22 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 23 |  |  |  | 24 |  | 1 |  |  | 0
|  |  | 0 |  |  | 1 |  | 25 |  |  |  | 26 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 27 |  |  |  | 28 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 29 |  |  |  | 30 |  | 1 |  |  | 0
|  |  | 0 |  |  | 1 |  | 31 |  |  |  | 32 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 33 |  |  |  | 34 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 35 |  |  |  | 36 |  | 1 |  |  | 0
|  |  | 0 |  |  | 1 |  | 37 |  |  |  | 38 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 39 |  |  |  | 40 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 41 |  |  |  | 42 |  | 1 |  |  | 0
|  |  | 0 |  |  | 1 |  | 43 |  |  |  | 44 |  | 1 | 0
|  |  |  | 0 |  | 1 |  | 45 |  |  |  | 46 |  | 1 |  | 0
[5 empty] | 0 | 1 |  | 47 |  |  |  | 48 |  | 1 |  |  | 0
Sub-total |  |  | 401 | 265.5 | 356.5 |  |  |  | R | Y | B |  |  |  | 273 | 375 | 332 |  | Sub-total
connected load (KVA) |  |  | 0.401 | 0.2655 | 0.3565 | [9 empty] | 0.273 | 0.375 | 0.332 |  | connected load (KW)
|  |  | 2.003 | Kwatt | [8 empty] | Total connected load "R" |  |  |  | 674 |  | Watt
[13 empty] | Total connected load "Y" |  |  |  | 640.5 |  | Watt
|  |  | 0.9 | [9 empty] | Total connected load "B" |  |  |  | 688.5 |  | Watt
[13 empty] | Difference between max & min Ph |  |  |  | 48
[13 empty] | % Diffrence |  |  |  | 6.9717
|  |  | 1.8027 | Kwatt | [8 empty] | Panel Balance Check |  |  | BALANCED
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C

## PP-G
Size of Cable (mm2) | Panel Name:- PP-G C.B :- 50A Cable :- 4*10+10 mm2 | [18 empty] | Size of Cable (mm2)
Feeder From :- MDP Panel Location:- GROUND FLOOR
| Description | Load | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | AMP Trip | PH | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Load | Description
3*4 | Normal Socket | 810 | 810 |  |  | 1 | 16 | 1 |  |  |  | 2 | 16 | 1 | 810 |  |  | 810 | Normal Socket | 3*4
3*4 | Normal Socket | 972 |  | 972 |  | 1 | 16 | 3 |  |  |  | 4 | 16 | 1 |  | 972 |  | 972 | Normal Socket | 3*4
3*4 | Normal Socket | 810 |  |  | 810 | 1 | 16 | 5 |  |  |  | 6 | 16 | 1 |  |  | 1134 | 1134 | Normal Socket | 3*4
3*4 | Normal Socket | 1134 | 1134 |  |  | 1 | 16 | 7 |  |  |  | 8 | 16 | 1 | 972 |  |  | 972 | Normal Socket | 3*4
3*4 | Normal Socket | 1134 |  | 1134 |  | 1 | 16 | 9 |  |  |  | 10 | 16 | 1 |  | 972 |  | 972 | Normal Socket | 3*4
3*4 | Normal Socket | 810 |  |  | 810 | 1 | 16 | 11 |  |  |  | 12 | 16 | 1 |  |  | 1296 | 1296 | Normal Socket | 3*4
3*4 | Normal Socket | 1134 | 1134 |  |  | 1 | 16 | 13 |  |  |  | 14 | 16 | 1 | 1296 |  |  | 1296 | Normal Socket | 3*4
3*4 | Normal Socket | 1134 |  | 1134 |  | 1 | 16 | 15 |  |  |  | 16 | 16 | 1 |  | 810 |  | 810 | Normal Socket | 3*4
3*4 | Normal Socket | 810 |  |  | 810 | 1 | 16 | 17 |  |  |  | 18 | 16 | 1 |  |  | 1134 | 1134 | Normal Socket | 3*4
3*4 | Heater | 1500 | 1500 |  |  | 1 | 25 | 19 |  |  |  | 20 | 25 | 1 | 1500 |  |  | 1500 | Heater | 3*4
3*4 | Heater | 1500 |  | 1500 |  | 1 | 25 | 21 |  |  |  | 22 | 25 | 1 |  | 1500 |  | 1500 | Heater | 3*4
3*4 | A/C | 1119 |  |  | 1119 | 1 | 25 | 23 |  |  |  | 24 | 25 | 1 |  |  | 1119 | 1119 | A/C | 3*4
3*4 | A/C | 1119 | 1119 |  |  | 1 | 25 | 25 |  |  |  | 26 | 25 | 1 | 746 |  |  | 746 | A/C | 3*3
3*4 | A/C | 1492 |  | 1492 |  | 1 | 16 | 27 |  |  |  | 28 | 32 | 1 |  | 1492 |  | 1492 | A/C | 3*4
3*3 | A/C | 746 |  |  | 746 | 1 | 32 | 29 |  |  |  | 30 | 16 | 1 |  |  | 1679 | 1679 | A/C | 3*4
3*4 | A/C | 1492 | 1492 |  |  | 1 | 32 | 31 |  |  |  | 32 | 32 | 1 | 1679 |  |  | 1679 | A/C | 3*4
3*4 | A/C | 1679 |  | 1679 |  | 1 | 32 | 33 |  |  |  | 34 | 16 | 1 |  | 746 |  | 746 | A/C | 3*3
3*3 | A/C | 746 |  |  | 746 | 1 | 16 | 35 |  |  |  | 36 | 16 | 1 |  |  | 2238 | 2238 | A/C | 3*3
3*4 | A/C | 1492 | 1492 |  |  | 1 | 16 | 37 |  |  |  | 38 | 32 | 1 | 746 |  |  | 746 | A/C | 3*6
3*4 | A/C | 1492 |  | 1492 |  | 1 | 40 | 39 |  |  |  | 40 | 32 | 1 |  | 1492 |  | 1492 | A/C | 3*4
3*4 | A/C | 1679 |  |  | 1679 | 1 | 32 | 41 | [10 empty] | spare
| spare |  | 0 |  |  |  |  | 43 |  |  |  | 44 |  |  | 0 |  |  |  | spare
| spare |  |  | 0 |  |  |  | 45 |  |  |  | 46 |  |  |  | 0 |  |  | spare
| spare |  |  |  | 0 |  |  | 47 |  |  |  | 48 |  |  |  |  | 0 |  | spare
Sub-total |  |  | 0 | [5 empty] | R | Y | B |  |  |  | 7749 | 7984 | 8600 |  | Sub-total
connected load (KW) |  |  | 0 | 0 | 0 | [9 empty] | 7.749 | 7.984 | 8.6 |  | connected load (KW)
|  |  | 24.333 | Kwatt | [8 empty] | Total connected load "R" |  |  |  | 7749 |  | Watt
[13 empty] | Total connected load "Y" |  |  |  | 7984 |  | Watt
|  |  | 0.8 | [9 empty] | Total connected load "B" |  |  |  | 8600 |  | Watt
[13 empty] | Difference between max & min Ph |  |  |  | 851
[13 empty] | % Diffrence |  |  |  | 9.8953
|  |  | 19.4664 | Kwatt | [8 empty] | Panel Balance Check |  |  | BALANCED
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C

## PP-F
Size of Cable (mm2) | Panel Name:- PP-F C.B :- 100A Cable :- 4*35+16 mm2 | [18 empty] | Size of Cable (mm2)
Feeder From :- MDP Panel Location:- GROUND FLOOR
| Description | Load | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | AMP Trip | PH | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Load | Description
3*4 | Normal Socket | 972 | 972 |  |  | 1 | 16 | 1 |  |  |  | 2 | 16 | 1 | 810 |  |  | 810 | Normal Socket | 3*4
3*4 | Normal Socket | 972 |  | 972 |  | 1 | 16 | 3 |  |  |  | 4 | 16 | 1 |  | 810 |  | 810 | Normal Socket | 3*4
3*4 | Normal Socket | 810 |  |  | 810 | 1 | 16 | 5 |  |  |  | 6 | 16 | 1 |  |  | 810 | 810 | Normal Socket | 3*4
3*4 | Normal Socket | 810 | 810 |  |  | 1 | 16 | 7 |  |  |  | 8 | 16 | 1 | 810 |  |  | 810 | Normal Socket | 3*4
3*4 | Normal Socket | 810 |  | 810 |  | 1 | 16 | 9 |  |  |  | 10 | 16 | 1 |  | 648 |  | 648 | Normal Socket | 3*4
3*4 | Normal Socket | 972 |  |  | 972 | 1 | 16 | 11 |  |  |  | 12 | 16 | 1 |  |  | 810 | 810 | Normal Socket | 3*4
3*4 | Normal Socket | 648 | 648 |  |  | 1 | 16 | 13 |  |  |  | 14 | 16 | 1 | 972 |  |  | 972 | Normal Socket | 3*4
3*4 | Normal Socket | 648 |  | 648 |  | 1 | 16 | 15 |  |  |  | 16 | 16 | 1 |  | 1134 |  | 1134 | Normal Socket | 3*4
3*4 | Normal Socket | 810 |  |  | 810 | 1 | 16 | 17 |  |  |  | 18 | 16 | 1 |  |  | 810 | 810 | Normal Socket | 3*4
3*4 | Normal Socket | 648 | 648 |  |  | 1 | 16 | 19 |  |  |  | 20 | 25 | 1 | 1500 |  |  | 1500 | Heater | 3*4
3*4 | Heater | 1500 |  | 1500 |  | 1 | 25 | 21 |  |  |  | 22 | 25 | 1 |  | 1500 |  | 1500 | Heater | 3*4
3*4 | Heater | 1500 |  |  | 1500 | 1 | 25 | 23 |  |  |  | 24 | 32 | 1 |  |  | 1678.5 | 1678.5 | A/C | 3*4
3*3 | A/C | 746 | 746 |  |  | 1 | 16 | 25 |  |  |  | 26 | 32 | 1 | 1678.5 |  |  | 1678.5 | A/C | 3*3
3*4 | A/C | 1119 |  | 1119 |  | 1 | 25 | 27 |  |  |  | 28 | 25 | 1 |  | 1119 |  | 1119 | A/C | 3*4
3*4 | A/C | 1119 |  |  | 1119 | 1 | 25 | 29 |  |  |  | 30 | 32 | 1 |  |  | 1492 | 1492 | A/C | 3*4
3*4 | A/C | 1492 | 1492 |  |  | 1 | 32 | 31 |  |  |  | 32 | 32 | 1 | 1678.5 |  |  | 1678.5 | A/C | 3*4
3*4 | A/C | 1492 |  | 1492 |  | 1 | 32 | 33 |  |  |  | 34 | 32 | 1 |  | 1678.5 |  | 1678.5 | A/C | 3*4
3*4 | A/C | 2238 |  |  | 2238 | 1 | 40 | 35 |  |  |  | 36 | 16 | 1 |  |  | 746 | 746 | A/C | 3*4
3*4 | A/C | 746 | 746 |  |  | 1 | 16 | 37 |  |  |  | 38 | 16 | 1 | 746 |  |  | 746 | A/C | 3*4
3*4 | A/C | 1492 |  | 1492 |  | 1 | 32 | 39 |  |  |  | 40 | 25 | 1 |  | 1119 |  | 1119 | A/C | 3*4
3*4 | A/C | 1492 |  |  | 1492 | 1 | 32 | 41 |  |  |  | 42 | 16 | 1 |  |  | 746 | 746 | A/C | 3*4
3*3 | A/C | 746 | 746 |  |  | 1 | 16 | 43 |  |  |  | 44 | 32 | 1 | 1492 |  |  | 1492 | A/C
| A/C | 1678.5 |  | 1678.5 |  | 1 | 32 | 45 |  |  |  | 46 |  |  |  | 0 |  |  | spare
| spare |  |  |  | 0 |  |  | 47 |  |  |  | 48 |  |  |  |  | 0 |  | spare
Sub-total |  |  | 6808 | 9711.5 | 8941 |  |  |  | R | Y | B |  |  |  | 9687 | 8008.5 | 7092.5 |  | Sub-total
connected load (KW) |  |  | 6.808 | 9.7115 | 8.941 | [9 empty] | 9.687 | 8.0085 | 7.0925 |  | connected load (KW)
|  |  | 50.2485 | Kwatt | [8 empty] | Total connected load "R" |  |  |  | 16495 |  | Watt
[13 empty] | Total connected load "Y" |  |  |  | 17720 |  | Watt
|  |  | 0.8 | [9 empty] | Total connected load "B" |  |  |  | 16033.5 |  | Watt
[13 empty] | Difference between max & min Ph |  |  |  | 1686.5
[13 empty] | % Diffrence |  |  |  | 9.5175
|  |  | 40.1988 | Kwatt | [8 empty] | Panel Balance Check |  |  | BALANCED
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C

## EDP
Size of Cable (mm2) | Panel Name:- EDP C.B :- 16A Cable :- 4*4+4mm2 | [18 empty] | Size of Cable (mm2)
Feeder From :- EMDP Panel Location:- GROUND FLOOR
| Description | Load | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | AMP Trip | PH | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Load | Description
3*2.5 | Lighting | 107 | 107 |  |  | 1 | 10 | 1 |  |  |  | 2 | 10 | 1 | 70.5 |  |  | 70.5 | Lighting (LCP) | 3*2.5
3*2.5 | Lighting (LCP) | 82.5 |  | 82.5 |  | 1 | 10 | 3 |  |  |  | 4 | 10 | 1 |  | 69 |  | 69 | Lighting (LCP) | 3*2.5
3*2.5 | Lighting | 124 |  |  | 124 | 1 | 10 | 5 |  |  |  | 6 | 10 | 1 |  |  | 94.5 | 94.5 | Lighting | 3*2.5
3*2.5 | Lighting | 101 | 101 |  |  | 1 | 10 | 7 |  |  |  | 8 | 10 | 1 | 42 |  |  | 42 | Lighting | 3*2.5
3*2.5 | Lighting | 148 |  | 148 |  | 1 | 10 | 9 |  |  |  | 10 | 16 | 1 |  | 63 |  | 63 | Lighting (LCP) | 3*2.5
3*2.5 | Lighting (LCP) | 78 |  |  | 78 | 1 | 16 | 11 |  |  |  | 12 | 16 | 1 |  |  | 63 | 63 | Lighting (LCP) | 3*2.5
3*2.5 | Lighting | 42 | 42 |  |  | 1 | 16 | 13 |  |  |  | 14 | 16 | 1 | 89 |  |  | 89 | Lighting | 3*2.5
3*2.5 | Lighting | 118 |  | 118 |  | 1 | 16 | 15 |  |  |  | 16 | 16 | 1 |  | 125 |  | 125 | Lighting | 3*2.5
3*2.5 | Lighting | 118 |  |  | 118 | 1 | 16 | 17 |  |  |  | 18 |  | 1 |  |  | 148 | 148 | Lighting | 3*2.5
3*2.5 | Lighting | 136 | 136 |  |  | 1 | 16 | 19 |  |  |  | 20 |  | 1 | 0 |  |  |  | spare
| spare |  |  | 0 |  | 1 |  | 21 |  |  |  | 22 |  | 1 |  | 0 |  |  | spare
| spare |  |  |  | 0 | 1 |  | 23 |  |  |  | 24 |  | 1 |  |  | 0 |  | spare
|  |  | 0 |  |  |  |  | 25 |  |  |  | 26 |  |  | 0
|  |  |  | 0 |  |  |  | 27 |  |  |  | 28 |  |  |  | 0
[5 empty] | 0 |  |  | 29 |  |  |  | 30 |  |  |  |  | 0
Sub-total |  |  | 386 | 348.5 | 320 |  |  |  | R | Y | B |  |  |  | 201.5 | 257 | 305.5 |  | Sub-total
connected load (KW) |  |  | 0.386 | 0.3485 | 0.32 | [9 empty] | 0.2015 | 0.257 | 0.3055 |  | connected load (KW)
|  |  | 1.8185 | Kwatt | [8 empty] | Total connected load "R" |  |  |  | 587.5 |  | Watt
[13 empty] | Total connected load "Y" |  |  |  | 605.5 |  | Watt
|  |  | 0.9 | [9 empty] | Total connected load "B" |  |  |  | 625.5 |  | Watt
[13 empty] | Difference between max & min Ph |  |  |  | 38
[13 empty] | % Diffrence |  |  |  | 6.0751
|  |  | 1.6366 | Kwatt | [8 empty] | Panel Balance Check |  |  | BALANCED
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C

## UPS-G
Size of Cable (mm2) | Panel Name:- UPS-G C.B :- 32A Cable :- 4*6+6 mm2 | [18 empty] | Size of Cable (mm2)
Feeder From :- EMDP Panel Location:- GROUND FLOOR
| Description | Load | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | AMP Trip | PH | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Load | Description
3*4 | UPS Socket | 648 | 648 |  |  | 1 | 10 | 1 |  |  |  | 2 | 10 | 1 | 648 |  |  | 648 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  | 972 |  | 1 | 10 | 3 |  |  |  | 4 | 10 | 1 |  | 972 |  | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  |  | 972 | 1 | 10 | 5 |  |  |  | 6 | 10 | 1 |  |  | 972 | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 648 | 648 |  |  | 1 | 10 | 7 |  |  |  | 8 | 10 | 1 | 972 |  |  | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  | 972 |  | 1 | 10 | 9 |  |  |  | 10 | 16 | 1 |  | 648 |  | 648 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  |  | 972 | 1 | 16 | 11 |  |  |  | 12 | 16 | 1 |  |  | 972 | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 648 | 648 |  |  | 1 | 16 | 13 |  |  |  | 14 | 16 | 1 | 972 |  |  | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  | 972 |  | 1 | 16 | 15 |  |  |  | 16 | 16 | 1 |  | 0
[5 empty] | 0 | 1 | 16 | 17 |  |  |  | 18 | 16 | 1 |  |  | 0
|  |  | 0 |  |  | 1 | 16 | 19 |  |  |  | 20 | 16 | 1 | 0
|  |  |  | 0 |  | 1 | 16 | 21 |  |  |  | 22 | 16 | 1 |  | 0
[5 empty] | 0 | 1 | 16 | 23 |  |  |  | 24 |  |  |  |  | 0
|  |  | 0 |  |  |  |  | 25 |  |  |  | 26 |  |  | 0
|  |  |  | 0 |  |  |  | 27 |  |  |  | 28 |  |  |  | 0
[5 empty] | 0 |  |  | 29 |  |  |  | 30 |  |  |  |  | 0
Sub-total |  |  | 1944 | 2916 | 1944 |  |  |  | R | Y | B |  |  |  | 2592 | 1620 | 1944 |  | Sub-total
connected load (KW) |  |  | 1.944 | 2.916 | 1.944 | [9 empty] | 2.592 | 1.62 | 1.944 |  | connected load (KW)
|  |  | 12.96 | Kwatt | [8 empty] | Total connected load "R" |  |  |  | 4536 |  | Watt
[13 empty] | Total connected load "Y" |  |  |  | 4536 |  | Watt
|  |  | 0.9 | [9 empty] | Total connected load "B" |  |  |  | 3888 |  | Watt
[13 empty] | Difference between max & min Ph |  |  |  | 648
[13 empty] | % Diffrence |  |  |  | 14.2857
|  |  | 11.664 | Kwatt | [8 empty] | Panel Balance Check |  |  | UNBALANCED
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C

## UPS-F
Size of Cable (mm2) | Panel Name:- UPS-F C.B :- 40A Cable :- 4*10+10 mm2 | [18 empty] | Size of Cable (mm2)
Feeder From :- EMDP Panel Location:- GROUND FLOOR
| Description | Load | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | AMP Trip | PH | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Load | Description
3*4 | UPS Socket | 972 | 972 |  |  | 1 | 10 | 1 |  |  |  | 2 | 10 | 1 | 972 |  |  | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 1296 |  | 1296 |  | 1 | 10 | 3 |  |  |  | 4 | 10 | 1 |  | 648 |  | 648 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  |  | 972 | 1 | 10 | 5 |  |  |  | 6 | 10 | 1 |  |  | 972 | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 | 972 |  |  | 1 | 10 | 7 |  |  |  | 8 | 10 | 1 | 972 |  |  | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  | 972 |  | 1 | 10 | 9 |  |  |  | 10 | 16 | 1 |  | 972 |  | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  |  | 972 | 1 | 16 | 11 |  |  |  | 12 | 16 | 1 |  |  | 972 | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 | 972 |  |  | 1 | 16 | 13 |  |  |  | 14 | 16 | 1 | 972 |  |  | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  | 972 |  | 1 | 16 | 15 |  |  |  | 16 | 16 | 1 |  | 972 |  | 972 | UPS Socket | 3*4
3*4 | UPS Socket | 972 |  |  | 972 | 1 | 16 | 17 |  |  |  | 18 | 16 | 1 |  |  | 1296 | 1296 | UPS Socket | 3*4
|  |  | 0 |  |  | 1 | 16 | 19 |  |  |  | 20 | 16 | 1 | 0
|  |  |  | 0 |  | 1 | 16 | 21 |  |  |  | 22 | 16 | 1 |  | 0
[5 empty] | 0 | 1 | 16 | 23 |  |  |  | 24 |  |  |  |  | 0
|  |  | 0 |  |  |  |  | 25 |  |  |  | 26 |  |  | 0
|  |  |  | 0 |  |  |  | 27 |  |  |  | 28 |  |  |  | 0
[5 empty] | 0 |  |  | 29 |  |  |  | 30 |  |  |  |  | 0
Sub-total |  |  | 2916 | 3240 | 2916 |  |  |  | R | Y | B |  |  |  | 2916 | 2592 | 3240 |  | Sub-total
connected load (KW) |  |  | 2.916 | 3.24 | 2.916 | [9 empty] | 2.916 | 2.592 | 3.24 |  | connected load (KW)
|  |  | 17.82 | Kwatt | [8 empty] | Total connected load "R" |  |  |  | 5832 |  | Watt
[13 empty] | Total connected load "Y" |  |  |  | 5832 |  | Watt
|  |  | 0.9 | [9 empty] | Total connected load "B" |  |  |  | 6156 |  | Watt
[13 empty] | Difference between max & min Ph |  |  |  | 324
[13 empty] | % Diffrence |  |  |  | 5.2632
|  |  | 16.038 | Kwatt | [8 empty] | Panel Balance Check |  |  | BALANCED
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C

## EMDP
Size of Cable (mm2) | Panel Name:- EMDP Mounted: SURFACE | [16 empty] | Size of Cable (mm2)
Feeder From :- MDP Panel Location:- GROUND FLOOR Main circuit breaker rating:- 80A Cable :- 4*25+16 mm2
| Description | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | PH | AMP Trip | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Description
4*4+4 | EDP | 587.5 | 605.5 | 625.5 | 3 | 16 | 1 |  |  |  | 2 | 3 | 32 | 4536 | 4536 | 3888 | UPS-G | 4*6+6
[7 empty] | 3 |  |  |  | 4
[7 empty] | 5 |  |  |  | 6
4*10+10 | UPS-F | 5832 | 5832 | 6156 | 3 | 40 | 7 |  |  |  | 8 | 3 |  |  |  |  | Spare
[7 empty] | 9 |  |  |  | 10
[7 empty] | 11 |  |  |  | 12
[7 empty] | 13 |  |  |  | 14
[7 empty] | 15 |  |  |  | 16
[7 empty] | 17 |  |  |  | 18
[7 empty] | 19 |  |  |  | 20
[7 empty] | 21 |  |  |  | 22
[7 empty] | 23 |  |  |  | 24
[7 empty] | 25 |  |  |  | 26
[7 empty] | 27 |  |  |  | 28
[7 empty] | 29 |  |  |  | 30
[5 empty] | 3 |  | 31 |  |  |  | 32 | 3
[7 empty] | 33 |  |  |  | 34
[7 empty] | 35 |  |  |  | 36
[5 empty] | 3 |  | 37 |  |  |  | 38 | 3
[7 empty] | 39 |  |  |  | 40
[7 empty] | 41 |  |  |  | 42
[5 empty] | 3 |  | 43 |  |  |  | 44 | 3
[7 empty] | 45 |  |  |  | 46
[7 empty] | 47 |  |  |  | 48
Sub-total |  | 6419.5 | 6437.5 | 6781.5 |  |  |  | R | Y | B |  |  |  | 4536 | 4536 | 3888 | Sub-total
connected load (KW) |  | 6.4195 | 6.4375 | 6.7815 | [9 empty] | 4.536 | 4.536 | 3.888 | connected load (KW)
|  | 32.5985 | Kwatt | [12 empty] | 10955.5 | Watt
[16 empty] | 10973.5 | Watt
|  | 0.9 | [13 empty] | 10669.5 | Watt
304
2.7703
|  | 29.3387 | Kwatt | [11 empty] | BALANCED
|  | 34.5161 | KVA
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C

## MDP
Size of Cable (mm2) | Panel Name:- MDP Mounted: SURFACE | [16 empty] | Size of Cable (mm2)
Feeder From :- TRANSFORMER Panel Location:- GROUND FLOOR Main circuit breaker rating:- 200A Cable :- 4*150+70 mm2
| Description | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | PH | AMP Trip | BR No. | R | Y | B | BR No. | PH | AMP Trip | Phase (R) (Watt) | Phase (Y) (Watt) | Phase (B) (Watt) | Description
4*3+3 | LP-G | 750 | 730 | 714.5 | 3 | 10 | 1 |  |  |  | 2 | 3 | 10 | 674 | 640.5 | 688.5 | LP-F | 4*3+3
[7 empty] | 3 |  |  |  | 4
[7 empty] | 5 |  |  |  | 6
4*10+10 | PP-G | 7749 | 7984 | 8600 | 3 | 50 | 7 |  |  |  | 8 | 3 | 100 | 16495 | 17720 | 16033.5 | PP-F | 4*35+16
[7 empty] | 9 |  |  |  | 10
[7 empty] | 11 |  |  |  | 12
4*25+16 | EMDP | 10955.5 | 10973.5 | 10669.5 | 3 | 80 | 13 |  |  |  | 14 | 3 |  |  |  |  | Spare
[7 empty] | 15 |  |  |  | 16
[7 empty] | 17 |  |  |  | 18
[5 empty] | 3 |  | 19 |  |  |  | 20 | 3
[7 empty] | 21 |  |  |  | 22
[7 empty] | 23 |  |  |  | 24
[5 empty] | 3 |  | 25 |  |  |  | 26 | 3
[7 empty] | 27 |  |  |  | 28
[7 empty] | 29 |  |  |  | 30
[5 empty] | 3 |  | 31 |  |  |  | 32 | 3
[7 empty] | 33 |  |  |  | 34
[7 empty] | 35 |  |  |  | 36
[5 empty] | 3 |  | 37 |  |  |  | 38 | 3
[7 empty] | 39 |  |  |  | 40
[7 empty] | 41 |  |  |  | 42
[5 empty] | 3 |  | 43 |  |  |  | 44 | 3
[7 empty] | 45 |  |  |  | 46
[7 empty] | 47 |  |  |  | 48
Sub-total |  | 19454.5 | 19687.5 | 19984 |  |  |  | R | Y | B |  |  |  | 17169 | 18360.5 | 16722 | Sub-total
connected load (KW) |  | 19.4545 | 19.6875 | 19.984 | [9 empty] | 17.169 | 18.3605 | 16.722 | connected load (KW)
|  | 111.3775 | Kwatt | [12 empty] | 36623.5 | Watt
[16 empty] | 38048 | Watt
|  | 0.8 | [13 empty] | 36706 | Watt
1424.5
3.744
|  | 89.102 | Kwatt | [11 empty] | BALANCED
|  | 104.8259 | KVA
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C
C